Indicative testing and inspection intervals for electrical equipment -  reproduced from AS/NZS 3760: 2010 (table 4)

| Type of Environment or Equipment | Interval between inspection and tests |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Equipment including Class I equipment, Class II equipment, cord sets, cord extension sets and EPODs | Residual Current Devices (RCDs) |  |  |  |
|  |  | Push Button test by user |  | Operating time and push-button test |  |
| a | b | Portable c | Fixed d | Portable e | Fixed f |
| Factories, workshops, places of manufacture, assembly, maintenance or fabrication | 6 months University Workshops | Daily, or Pre-Use | 6 Months | 12 Months | 12 Months |
| Environment where the equipment or supply flexible cord is subject to flexing in normal use OR is open to abuse OR is in a hostile environment | 12 months University Labs and Fieldwork | 3 Months | 6 Months | 12 Months | 12 Months |
| Environment where the equipment or supply flexible cord is not subject to flexing in normal use OR is not open to abuse OR is not in a hostile environment | 5 years Office Equipment | 3 Months | 6 Months | 2 years | 2 years |
| Residential type areas e.g. hotels, residential institutions, motels, boarding houses, halls, hostels, accommodation houses etc | 2 years | 6 Months | 6 Months | 2 years | 2 years |
| Equipment used for commercial cleaning | 6 months | Daily, or Pre-Use | NA | 6 Months | NA |
| Hire Equipment Inspection Test and Tag | Prior to hire | Including push-button test by hirer prior to hire |  | NA | NA |
|  | 3 months | NA |  | 3 Months | 12 Months |
| Repaired, serviced or second-hand equipment | After repair or service which could affect electrical safety or on reintroduction to service: Refer to AS/NZS5762 |  |  |  |  |